## Tacoma Power Terms & Conditions
To complete the Terms & Conditions, double-click the icon below:

## Requirements & Checklists
Project Qualifications & Requirements:
1) | For existing units only - not for new construction.
2) | Existing units must be constant volume single zone packaged RTU’s.
3) | Minimum 2,000 annual operating hours.
4) | Pre-approval is required.
5) | Manufactured date of units must be ≤ 20 years old.
6) | Units must be in good working order and have a functional air-side economizer.
7) | Unit cooling capacity must be 5 tons or greater.
8) | Supply fan motor must be 1 horsepower minimum with 3-phase power supply.
9) | Supply fan must operate continuously during occupied hours.
Supply fan currently set at "Auto" is eligible for the Program given that it will be "ON continuously" and controlled by ARC.
ARC Technical Requirements:
1) | Variable speed, multi-speed or cycling of the supply fan that meets ventilation and space conditioning needs per ASHRAE 62.1
or local jurisdiction code requirements.
2) | Digital, integrated economizer control (ARC-Full only).
3) | CO2 Demand Control Ventilation (ARC-Full only).
Notes:
1) | Make sure building pressure balance is maintained at acceptable levels.
2) | In limited cases, installation of ARC equipment on RTUs may result in damage to motors.
Consult your installer to verify proper RTU operations and compatibility with ARC equipment.
Utilities participating in the ARC rebate program are not responsible for equipment or equipment installation.
2) | Final rebate amounts are capped at 70% of total project cost (after tax).
3) | Electrical savings estimates are based on 2015 BPA Implementation Manual. Gas savings are averaged for recent installations in the region.
Site savings may vary depending on RTU type, operating schedules and space served.
Annual electrical and gas bill savings are estimated. Actual bill savings will vary by utility and rate schedule.
Application Checklist |  |  | Completion Checklist
| Utility Application. |  |  | Invoice.
| Joint Utility Rebate Worksheet. |  |  | Photos of units with controller and of VSD and general rooftop view.
| Bid/Cost Proposal. |  |  | Submit a Utility ARC Startup Form (one per unit). Installer start up forms can be provided in lieu of the Utility ARC Start Up Form if all information from the ARC Start Up Form is documented within the installer start up form.
Photos of existing RTU (unit and fan motor nameplates).
Specific locations of RTU’s that are affected by project.
Notes on satellite images or schematics of rooftop with RTU’s.
Process Flow
1) | Submit/Email all items on the Application Checklist to your Electric Utility rep. The Utility rep will contact you if a site verification is required.
2) | Electricity Utility will coordinate with PSE and finalize cost share and rebate amounts.
4) | Utility will prepare and send agreement package to Customer for signature after it passes internal review.
5) | Utility will notify the Customer upon receipt of signed agreement back.
6) | Contractor orders equipment and proceeds with installation.
7) | Submit all items on the Completion Checklist and contact Utility representative when the installation is complete.
9) | Utility will review submitted information and perform M&V evaluation.
10) | Utility will inform Customer and Contractor of final savings and rebate amount.
11) | Utility will process the rebate payment and send check to Customer or assigned Recipient.
Contacts & Websites
_ | Puget Sound Energy | Dan Myers |  | (360) 786-5934 | dan.myers@pse.com
_ | Seattle City Light | Energy Advisors |  | (206) 684-3800 | sclenergyadvisor@seattle.gov
_ | Snohomish PUD | Sinh Tran |  | (425) 783-8248 | svtran@snopud.com
_ | Tacoma Power | Conservation - Commercial/Industrial |  | (253)-502-8619 | bizrebates@cityoftacoma.org
_ | Puget Sound Energy | www.pse.com | _ | Snohomish PUD | www.snopud.com
_ | Seattle City Light | www.seattle.gov/light/conserve | _ | Tacoma Power | www.mytpu.org/tacomapower
Joint Utility ARC Rebate Workbook V2.0
JOINT UTILITY REBATE PROGRAM
ADVANCED ROOFTOP UNIT CONTROL (ARC)
Program Requirements & Checklists
Units that do not meet these requirements may be eligible for a custom incentive. Contact your electric utility rep for more information.
Additional M&V may be required before and/or after installation based on utility discretion for large projects. Contact the applicable utility rep for more information.

## Rebate Worksheet
Project ID
Project Engineer
Date
Complete the green areas. Grey areas are auto filled.
Facility Name: |  |  |  |  | Business Type: |  |  |  | Electric Utility:
Street Address: |  |  |  | City: |  |  | Zip Code: |  | Gas Utility:
Contact Name: |  |  |  | Phone: |  |  | Email:
Existing Equipment | [12 empty] | ARC-Full |  |  |  | ARC-Lite
Unit ID | ARC Type | Unit Type | Cooling Btu/h (≥ 54,000 Btu/h) | Rounded Cooling Tonnage (≥ 5 tons) | Manufactured Year | Unit Age (≤ 20 yrs) | Fan Motor HP (≥ 1 HP) | Motor Phase (3-phase) | Operating Hours per Year (≥ 2,000 hours) | Eligible for Rebate? | Eligibility | For Savings Calculations | Electric Savings | Rebate for Electric Savings | Gas Savings | Rebate for Gas Savings | Electric Savings | Rebate for Electric Savings
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0
Proposed Equipment, Installer Info & Cost
Installer Company |  |  | Contact Name |  | Email |  |  | Phone |  | Project Cost*
ARC-Full Product Name: | [5 empty] | ARC-Lite Product Name:
* Cost should include equipment, labor, permit and tax.
Average Unit Annual Energy Savings and Rebate per Ton
Operating Hours per Year |  |  | ARC-Full | [5 empty] | ARC-Lite
|  |  | kWh/yr/ton Savings | Rebate per Ton | Therms/yr/ton Savings |  | Rebate per Ton (PSE Customers only) |  | kWh/yr/ton Savings | Rebate per Ton
Between 2,000 and 4,000 |  |  | 800 | 225 | 9.5 |  | 50 |  | 540 | 150
Greater than 4,000 |  |  | 1200 | [5 empty] | 810
Total Eligible Tonnage for Heat Pumps (nearest ton): |  |  |  |  | Total Eligible Tonnage for Gas Packs (nearest ton):
Total Annual Electric Savings (kWh/yr.): |  |  |  |  | Total Annual Gas Savings (therm/yr.):
Project Cost & Incentive |  |  |  |  | Customer's Economic Analysis
% Rebate Adjustment (rebate capped at 70% of cost): |  |  |  |  | Customer Net Cost: | [5 empty] | Max Potential Incentive
Adjusted Rebate for Electric Utility: |  |  |  |  | % Customer Cost: | [5 empty] | 0 | for electric savings
Adjusted Rebate for Gas Utility: |  |  |  |  | Total Bill Savings per Year (at 8¢/kWh and $1/therm avg.): | [5 empty] | 0 | for electric and gas savings
Total Rebate: |  |  |  |  | Customer Project Simple Payback: |  |  |  |  | #N/A | 0 | combined
% Rebate: |  |  |  |  | Customer Return on Investment (ROI): |  |  |  |  | #N/A
|  | combined | electric | gas | [5 empty] | Joint Utility ARC Rebate Workbook V2.0
Formulas:
Unit Age (≤ 20 yrs) = IF([Business Type:]="","",(YEAR(TODAY())-[Business Type:]))
JOINT UTILITY REBATE PROGRAM
ADVANCED ROOFTOP UNIT CONTROL (ARC)
Project Rebate Worksheet

## QPL (hidden)
Advanced Rooftop Unit Control Retrofit
Qualified Products List
Revised 6/16/2016
Full Retrofit:
Transformative Wave | TransformativeWave | CATALYST with eIQ
Pelican | Pelican | TS200 Thermostat
TS250 Thermostat
ARC-Full
Transformative Wave CATALYST with eIQ
Pelican TS200 TStat w/ Pearl Econ, Wireless Gateway & VSD
Pelican TS250 TStat w/ Pearl Econ, Wireless Gateway & VSD
Not on List. Please see Submittal
N/A
ARC-Lite:
Transformative Wave | TransformativeWave | CATALYST Lite
Lennox | Lennox | ARC with DCV
Trane | Trane | ARC with DCV
NextRev | NextRev | DrivePak
Pelican | Pelican | TS200 Thermostat
TS250 Thermostat
ARC Make & Model
Transformative Wave CATALYST with eIQ
Pelican TS200 TStat w/ Pearl Econ, Wireless Gateway & VSD
Pelican TS250 TStat w/ Pearl Econ, Wireless Gateway & VSD
Transformative Wave CATALYST Lite
Lennox ARC with DCV
Trane ARC with DCV
NextRev DrivePak
Pelican TS200 Thermostat
Pelican TS200 Thermostat
Not on List. Please see Submittal
N/A
*w/ Pearl Economizer, Extended Range Wireless Gateway, and VSD
Occupancy Type | Phase
Agricultural | Single
Aircraft Hangar | 3-Phase
Airport Operations
Animal Hospital | YesNo
Apartments & Condos | Yes
Bank | No
Casino
Cell Tower | Heat Type
Church | Gas
Church / School | Electric
Clinic | None
Communication
Conference Center | Voltage
Data Center | 208
Daycare | 460
District Facility | 575
Federal Government
FPD | ElectricUtility | GasUtility
Hospital | Puget Sound Energy | Puget Sound Energy
Hotel / Motel | Seattle City Light | None
Industrial & Manufacturing | Snohomish PUD
Library | Tacoma Power
Local Government
Medical & Dental | Unit Type
Non-profit | Gas Pack
Nursing & Retirement Homes | Heat Pump
Office Buildings
Other - Commercial | Supply Fan Control
Other - Industrial | Step
Parking Garage | VSD
Recreational
Research Lab | Status
Restaurant & Tavern | On
Retail Trade & Services | Off
School
Senior Center | Control Type
Storage | ARC-Full
Transportation | ARC-Lite
Warehouse
Water / Wastewater
Wholesale & Retail Food
Other

## ARC Start Up Form
ADVANCED ROOFTOP UNIT CONTROL (ARC)
ARC Start Up Form
Facility Name: |  |  | Project ID:
Facility Address: |  |  | Project Engineer:
Unit ID: |  |  | Click button for an additional sheet.
Unit Type: | Cooling Tonnage: |  | Motor HP:
Make: | Heat Type: |  | Motor FLA:
Model: | Heater Size: |  | Voltage:
Functional Testing
Date: |  |  | VSD Installed?
Time: |  |  | CO2 DCV Installed? (ARC-Full Only)
OSA Temp: |  |  | Code Minimum Ventilation Air Volume Met?
Status | OSA Damper % Open | Fan % Speed | Compressor On/Off | Heat On/Off
Off
Ventilation (Fan Only) Mode
Economizer Mode
1st Stage Cooling
2nd Stage Cooling
3rd Stage Cooling
1st Stage Heating
2nd Stage Heating
Notes
Installer Company: |  | Technician Name:
Joint Utility ARC Rebate Workbook V2.0
Additional Sheet

## ARC Start Up Form (2) (hidden)
ADVANCED ROOFTOP UNIT CONTROL (ARC)
ARC Start Up Form
Facility Name: |  |  |  | Project ID:
Facility Address: | , WA |  |  | Project Engineer:
Unit ID: |  |  |  | Click button for an additional sheet.
Unit Type: |  | Cooling Tonnage: |  | Motor HP:
Make: |  | Heat Type: |  | Motor FLA:
Model: |  | Heater Size: |  | Voltage:
Functional Testing
Date: |  |  |  | VSD Installed?
Time: |  |  |  | CO2 DCV Installed?
OSA Temp: |  |  |  | Code Minimum Ventilation Air Volume Met?
Status |  | OSA Damper % Open | Fan % Speed | Compressor On/Off | Heat On/Off
Off
Ventilation (Fan Only) Mode
Economizer Mode
1st Stage Cooling
2nd Stage Cooling
3rd Stage Cooling
1st Stage Heating
2nd Stage Heating
Notes
Installer Company: |  |  | Technician Name:
Joint Utility ARC Rebate Workbook V2.0
Additional Sheet

## ARC Start Up Form (3) (hidden)
ADVANCED ROOFTOP UNIT CONTROL (ARC)
ARC Start Up Form
Facility Name: |  |  |  | Project ID:
Facility Address: | , WA |  |  | Project Engineer:
Unit ID: |  |  |  | Click button for an additional sheet.
Unit Type: |  | Cooling Tonnage: |  | Motor HP:
Make: |  | Heat Type: |  | Motor FLA:
Model: |  | Heater Size: |  | Voltage:
Functional Testing
Date: |  |  |  | VSD Installed?
Time: |  |  |  | CO2 DCV Installed?
OSA Temp: |  |  |  | Code Minimum Ventilation Air Volume Met?
Status |  | OSA Damper % Open | Fan % Speed | Compressor On/Off | Heat On/Off
Off
Ventilation (Fan Only) Mode
Economizer Mode
1st Stage Cooling
2nd Stage Cooling
3rd Stage Cooling
1st Stage Heating
2nd Stage Heating
Notes
Installer Company: |  |  | Technician Name:
Joint Utility ARC Rebate Workbook V2.0
Additional Sheet

## ARC Start Up Form (4) (hidden)
ADVANCED ROOFTOP UNIT CONTROL (ARC)
ARC Start Up Form
Facility Name: |  |  |  | Project ID:
Facility Address: | , WA |  |  | Project Engineer:
Unit ID: |  |  |  | Click button for an additional sheet.
Unit Type: |  | Cooling Tonnage: |  | Motor HP:
Make: |  | Heat Type: |  | Motor FLA:
Model: |  | Heater Size: |  | Voltage:
Functional Testing
Date: |  |  |  | VSD Installed?
Time: |  |  |  | CO2 DCV Installed?
OSA Temp: |  |  |  | Code Minimum Ventilation Air Volume Met?
Status |  | OSA Damper % Open | Fan % Speed | Compressor On/Off | Heat On/Off
Off
Ventilation (Fan Only) Mode
Economizer Mode
1st Stage Cooling
2nd Stage Cooling
3rd Stage Cooling
1st Stage Heating
2nd Stage Heating
Notes
Installer Company: |  |  | Technician Name:
Joint Utility ARC Rebate Workbook V2.0
Additional Sheet

## ARC Start Up Form (5) (hidden)
ADVANCED ROOFTOP UNIT CONTROL (ARC)
ARC Start Up Form
Facility Name: |  |  |  | Project ID:
Facility Address: | , WA |  |  | Project Engineer:
Unit ID: |  |  |  | Click button for an additional sheet.
Unit Type: |  | Cooling Tonnage: |  | Motor HP:
Make: |  | Heat Type: |  | Motor FLA:
Model: |  | Heater Size: |  | Voltage:
Functional Testing
Date: |  |  |  | VSD Installed?
Time: |  |  |  | CO2 DCV Installed?
OSA Temp: |  |  |  | Code Minimum Ventilation Air Volume Met?
Status |  | OSA Damper % Open | Fan % Speed | Compressor On/Off | Heat On/Off
Off
Ventilation (Fan Only) Mode
Economizer Mode
1st Stage Cooling
2nd Stage Cooling
3rd Stage Cooling
1st Stage Heating
2nd Stage Heating
Notes
Installer Company: |  |  | Technician Name:
Joint Utility ARC Rebate Workbook V2.0
Additional Sheet

## ARC Start Up Form (6) (hidden)
ADVANCED ROOFTOP UNIT CONTROL (ARC)
ARC Start Up Form
Facility Name: |  |  |  | Project ID:
Facility Address: | , WA |  |  | Project Engineer:
Unit ID: |  |  |  | Click button for an additional sheet.
Unit Type: |  | Cooling Tonnage: |  | Motor HP:
Make: |  | Heat Type: |  | Motor FLA:
Model: |  | Heater Size: |  | Voltage:
Functional Testing
Date: |  |  |  | VSD Installed?
Time: |  |  |  | CO2 DCV Installed?
OSA Temp: |  |  |  | Code Minimum Ventilation Air Volume Met?
Status |  | OSA Damper % Open | Fan % Speed | Compressor On/Off | Heat On/Off
Off
Ventilation (Fan Only) Mode
Economizer Mode
1st Stage Cooling
2nd Stage Cooling
3rd Stage Cooling
1st Stage Heating
2nd Stage Heating
Notes
Installer Company: |  |  | Technician Name:
Joint Utility ARC Rebate Workbook V2.0
Additional Sheet

## ARC Start Up Form (7) (hidden)
ADVANCED ROOFTOP UNIT CONTROL (ARC)
ARC Start Up Form
Facility Name: |  |  |  | Project ID:
Facility Address: | , WA |  |  | Project Engineer:
Unit ID: |  |  |  | Click button for an additional sheet.
Unit Type: |  | Cooling Tonnage: |  | Motor HP:
Make: |  | Heat Type: |  | Motor FLA:
Model: |  | Heater Size: |  | Voltage:
Functional Testing
Date: |  |  |  | VSD Installed?
Time: |  |  |  | CO2 DCV Installed?
OSA Temp: |  |  |  | Code Minimum Ventilation Air Volume Met?
Status |  | OSA Damper % Open | Fan % Speed | Compressor On/Off | Heat On/Off
Off
Ventilation (Fan Only) Mode
Economizer Mode
1st Stage Cooling
2nd Stage Cooling
3rd Stage Cooling
1st Stage Heating
2nd Stage Heating
Notes
Installer Company: |  |  | Technician Name:
Joint Utility ARC Rebate Workbook V2.0
Additional Sheet

## ARC Start Up Form (8) (hidden)
ADVANCED ROOFTOP UNIT CONTROL (ARC)
ARC Start Up Form
Facility Name: |  |  |  | Project ID:
Facility Address: | , WA |  |  | Project Engineer:
Unit ID: |  |  |  | Click button for an additional sheet.
Unit Type: |  | Cooling Tonnage: |  | Motor HP:
Make: |  | Heat Type: |  | Motor FLA:
Model: |  | Heater Size: |  | Voltage:
Functional Testing
Date: |  |  |  | VSD Installed?
Time: |  |  |  | CO2 DCV Installed?
OSA Temp: |  |  |  | Code Minimum Ventilation Air Volume Met?
Status |  | OSA Damper % Open | Fan % Speed | Compressor On/Off | Heat On/Off
Off
Ventilation (Fan Only) Mode
Economizer Mode
1st Stage Cooling
2nd Stage Cooling
3rd Stage Cooling
1st Stage Heating
2nd Stage Heating
Notes
Installer Company: |  |  | Technician Name:
Joint Utility ARC Rebate Workbook V2.0
Additional Sheet

## ARC Start Up Form (9) (hidden)
ADVANCED ROOFTOP UNIT CONTROL (ARC)
ARC Start Up Form
Facility Name: |  |  |  | Project ID:
Facility Address: | , WA |  |  | Project Engineer:
Unit ID: |  |  |  | Click button for an additional sheet.
Unit Type: |  | Cooling Tonnage: |  | Motor HP:
Make: |  | Heat Type: |  | Motor FLA:
Model: |  | Heater Size: |  | Voltage:
Functional Testing
Date: |  |  |  | VSD Installed?
Time: |  |  |  | CO2 DCV Installed?
OSA Temp: |  |  |  | Code Minimum Ventilation Air Volume Met?
Status |  | OSA Damper % Open | Fan % Speed | Compressor On/Off | Heat On/Off
Off
Ventilation (Fan Only) Mode
Economizer Mode
1st Stage Cooling
2nd Stage Cooling
3rd Stage Cooling
1st Stage Heating
2nd Stage Heating
Notes
Installer Company: |  |  | Technician Name:
Joint Utility ARC Rebate Workbook V2.0
Additional Sheet

## ARC Start Up Form (10) (hidden)
ADVANCED ROOFTOP UNIT CONTROL (ARC)
ARC Start Up Form
Facility Name: |  |  |  | Project ID:
Facility Address: | , WA |  |  | Project Engineer:
Unit ID: |  |  |  | Click button for an additional sheet.
Unit Type: |  | Cooling Tonnage: |  | Motor HP:
Make: |  | Heat Type: |  | Motor FLA:
Model: |  | Heater Size: |  | Voltage:
Functional Testing
Date: |  |  |  | VSD Installed?
Time: |  |  |  | CO2 DCV Installed?
OSA Temp: |  |  |  | Code Minimum Ventilation Air Volume Met?
Status |  | OSA Damper % Open | Fan % Speed | Compressor On/Off | Heat On/Off
Off
Ventilation (Fan Only) Mode
Economizer Mode
1st Stage Cooling
2nd Stage Cooling
3rd Stage Cooling
1st Stage Heating
2nd Stage Heating
Notes
Installer Company: |  |  | Technician Name:
Joint Utility ARC Rebate Workbook V2.0
Additional Sheet

## ARC Start Up Form (11) (hidden)
ADVANCED ROOFTOP UNIT CONTROL (ARC)
ARC Start Up Form
Facility Name: |  |  |  | Project ID:
Facility Address: | , WA |  |  | Project Engineer:
Unit ID: |  |  |  | Click button for an additional sheet.
Unit Type: |  | Cooling Tonnage: |  | Motor HP:
Make: |  | Heat Type: |  | Motor FLA:
Model: |  | Heater Size: |  | Voltage:
Functional Testing
Date: |  |  |  | VSD Installed?
Time: |  |  |  | CO2 DCV Installed?
OSA Temp: |  |  |  | Code Minimum Ventilation Air Volume Met?
Status |  | OSA Damper % Open | Fan % Speed | Compressor On/Off | Heat On/Off
Off
Ventilation (Fan Only) Mode
Economizer Mode
1st Stage Cooling
2nd Stage Cooling
3rd Stage Cooling
1st Stage Heating
2nd Stage Heating
Notes
Installer Company: |  |  | Technician Name:
Joint Utility ARC Rebate Workbook V2.0
Additional Sheet

## ARC Start Up Form (12) (hidden)
ADVANCED ROOFTOP UNIT CONTROL (ARC)
ARC Start Up Form
Facility Name: |  |  |  | Project ID:
Facility Address: | , WA |  |  | Project Engineer:
Unit ID: |  |  |  | Click button for an additional sheet.
Unit Type: |  | Cooling Tonnage: |  | Motor HP:
Make: |  | Heat Type: |  | Motor FLA:
Model: |  | Heater Size: |  | Voltage:
Functional Testing
Date: |  |  |  | VSD Installed?
Time: |  |  |  | CO2 DCV Installed?
OSA Temp: |  |  |  | Code Minimum Ventilation Air Volume Met?
Status |  | OSA Damper % Open | Fan % Speed | Compressor On/Off | Heat On/Off
Off
Ventilation (Fan Only) Mode
Economizer Mode
1st Stage Cooling
2nd Stage Cooling
3rd Stage Cooling
1st Stage Heating
2nd Stage Heating
Notes
Installer Company: |  |  | Technician Name:
Joint Utility ARC Rebate Workbook V2.0
Additional Sheet

## ARC Start Up Form (13) (hidden)
ADVANCED ROOFTOP UNIT CONTROL (ARC)
ARC Start Up Form
Facility Name: |  |  |  | Project ID:
Facility Address: | , WA |  |  | Project Engineer:
Unit ID: |  |  |  | Click button for an additional sheet.
Unit Type: |  | Cooling Tonnage: |  | Motor HP:
Make: |  | Heat Type: |  | Motor FLA:
Model: |  | Heater Size: |  | Voltage:
Functional Testing
Date: |  |  |  | VSD Installed?
Time: |  |  |  | CO2 DCV Installed?
OSA Temp: |  |  |  | Code Minimum Ventilation Air Volume Met?
Status |  | OSA Damper % Open | Fan % Speed | Compressor On/Off | Heat On/Off
Off
Ventilation (Fan Only) Mode
Economizer Mode
1st Stage Cooling
2nd Stage Cooling
3rd Stage Cooling
1st Stage Heating
2nd Stage Heating
Notes
Installer Company: |  |  | Technician Name:
Joint Utility ARC Rebate Workbook V2.0
Additional Sheet

## ARC Start Up Form (14) (hidden)
ADVANCED ROOFTOP UNIT CONTROL (ARC)
ARC Start Up Form
Facility Name: |  |  |  | Project ID:
Facility Address: | , WA |  |  | Project Engineer:
Unit ID: |  |  |  | Click button for an additional sheet.
Unit Type: |  | Cooling Tonnage: |  | Motor HP:
Make: |  | Heat Type: |  | Motor FLA:
Model: |  | Heater Size: |  | Voltage:
Functional Testing
Date: |  |  |  | VSD Installed?
Time: |  |  |  | CO2 DCV Installed?
OSA Temp: |  |  |  | Code Minimum Ventilation Air Volume Met?
Status |  | OSA Damper % Open | Fan % Speed | Compressor On/Off | Heat On/Off
Off
Ventilation (Fan Only) Mode
Economizer Mode
1st Stage Cooling
2nd Stage Cooling
3rd Stage Cooling
1st Stage Heating
2nd Stage Heating
Notes
Installer Company: |  |  | Technician Name:
Joint Utility ARC Rebate Workbook V2.0
Additional Sheet

## ARC Start Up Form (15) (hidden)
ADVANCED ROOFTOP UNIT CONTROL (ARC)
ARC Start Up Form
Facility Name: |  |  |  | Project ID:
Facility Address: | , WA |  |  | Project Engineer:
Unit ID: |  |  |  | Click button for an additional sheet.
Unit Type: |  | Cooling Tonnage: |  | Motor HP:
Make: |  | Heat Type: |  | Motor FLA:
Model: |  | Heater Size: |  | Voltage:
Functional Testing
Date: |  |  |  | VSD Installed?
Time: |  |  |  | CO2 DCV Installed?
OSA Temp: |  |  |  | Code Minimum Ventilation Air Volume Met?
Status |  | OSA Damper % Open | Fan % Speed | Compressor On/Off | Heat On/Off
Off
Ventilation (Fan Only) Mode
Economizer Mode
1st Stage Cooling
2nd Stage Cooling
3rd Stage Cooling
1st Stage Heating
2nd Stage Heating
Notes
Installer Company: |  |  | Technician Name:
Joint Utility ARC Rebate Workbook V2.0
Additional Sheet

## ARC Start Up Form (16) (hidden)
ADVANCED ROOFTOP UNIT CONTROL (ARC)
ARC Start Up Form
Facility Name: |  |  |  | Project ID:
Facility Address: | , WA |  |  | Project Engineer:
Unit ID: |  |  |  | Click button for an additional sheet.
Unit Type: |  | Cooling Tonnage: |  | Motor HP:
Make: |  | Heat Type: |  | Motor FLA:
Model: |  | Heater Size: |  | Voltage:
Functional Testing
Date: |  |  |  | VSD Installed?
Time: |  |  |  | CO2 DCV Installed?
OSA Temp: |  |  |  | Code Minimum Ventilation Air Volume Met?
Status |  | OSA Damper % Open | Fan % Speed | Compressor On/Off | Heat On/Off
Off
Ventilation (Fan Only) Mode
Economizer Mode
1st Stage Cooling
2nd Stage Cooling
3rd Stage Cooling
1st Stage Heating
2nd Stage Heating
Notes
Installer Company: |  |  | Technician Name:
Joint Utility ARC Rebate Workbook V2.0
Additional Sheet

## ARC Start Up Form (17) (hidden)
ADVANCED ROOFTOP UNIT CONTROL (ARC)
ARC Start Up Form
Facility Name: |  |  |  | Project ID:
Facility Address: | , WA |  |  | Project Engineer:
Unit ID: |  |  |  | Click button for an additional sheet.
Unit Type: |  | Cooling Tonnage: |  | Motor HP:
Make: |  | Heat Type: |  | Motor FLA:
Model: |  | Heater Size: |  | Voltage:
Functional Testing
Date: |  |  |  | VSD Installed?
Time: |  |  |  | CO2 DCV Installed?
OSA Temp: |  |  |  | Code Minimum Ventilation Air Volume Met?
Status |  | OSA Damper % Open | Fan % Speed | Compressor On/Off | Heat On/Off
Off
Ventilation (Fan Only) Mode
Economizer Mode
1st Stage Cooling
2nd Stage Cooling
3rd Stage Cooling
1st Stage Heating
2nd Stage Heating
Notes
Installer Company: |  |  | Technician Name:
Joint Utility ARC Rebate Workbook V2.0
Additional Sheet

## ARC Start Up Form (18) (hidden)
ADVANCED ROOFTOP UNIT CONTROL (ARC)
ARC Start Up Form
Facility Name: |  |  |  | Project ID:
Facility Address: | , WA |  |  | Project Engineer:
Unit ID: |  |  |  | Click button for an additional sheet.
Unit Type: |  | Cooling Tonnage: |  | Motor HP:
Make: |  | Heat Type: |  | Motor FLA:
Model: |  | Heater Size: |  | Voltage:
Functional Testing
Date: |  |  |  | VSD Installed?
Time: |  |  |  | CO2 DCV Installed?
OSA Temp: |  |  |  | Code Minimum Ventilation Air Volume Met?
Status |  | OSA Damper % Open | Fan % Speed | Compressor On/Off | Heat On/Off
Off
Ventilation (Fan Only) Mode
Economizer Mode
1st Stage Cooling
2nd Stage Cooling
3rd Stage Cooling
1st Stage Heating
2nd Stage Heating
Notes
Installer Company: |  |  | Technician Name:
Joint Utility ARC Rebate Workbook V2.0
Additional Sheet

## ARC Start Up Form (19) (hidden)
ADVANCED ROOFTOP UNIT CONTROL (ARC)
ARC Start Up Form
Facility Name: |  |  |  | Project ID:
Facility Address: | , WA |  |  | Project Engineer:
Unit ID: |  |  |  | Click button for an additional sheet.
Unit Type: |  | Cooling Tonnage: |  | Motor HP:
Make: |  | Heat Type: |  | Motor FLA:
Model: |  | Heater Size: |  | Voltage:
Functional Testing
Date: |  |  |  | VSD Installed?
Time: |  |  |  | CO2 DCV Installed?
OSA Temp: |  |  |  | Code Minimum Ventilation Air Volume Met?
Status |  | OSA Damper % Open | Fan % Speed | Compressor On/Off | Heat On/Off
Off
Ventilation (Fan Only) Mode
Economizer Mode
1st Stage Cooling
2nd Stage Cooling
3rd Stage Cooling
1st Stage Heating
2nd Stage Heating
Notes
Installer Company: |  |  | Technician Name:
Joint Utility ARC Rebate Workbook V2.0
Additional Sheet

## ARC Start Up Form (20) (hidden)
ADVANCED ROOFTOP UNIT CONTROL (ARC)
ARC Start Up Form
Facility Name: |  |  |  | Project ID:
Facility Address: | , WA |  |  | Project Engineer:
Unit ID:
Unit Type: |  | Cooling Tonnage: |  | Motor HP:
Make: |  | Heat Type: |  | Motor FLA:
Model: |  | Heater Size: |  | Voltage:
Functional Testing
Date: |  |  |  | VSD Installed?
Time: |  |  |  | CO2 DCV Installed?
OSA Temp: |  |  |  | Code Minimum Ventilation Air Volume Met?
Status |  | OSA Damper % Open | Fan % Speed | Compressor On/Off | Heat On/Off
Off
Ventilation (Fan Only) Mode
Economizer Mode
1st Stage Cooling
2nd Stage Cooling
3rd Stage Cooling
1st Stage Heating
2nd Stage Heating
Notes
Installer Company: |  |  | Technician Name:
Joint Utility ARC Rebate Workbook V2.0